## Slide 1: OPW EVR PHASE 1 TRAINING Course
This class will cover how OPW equipment gets installed according to the manufactures installation instructions.
Notes: This course I designed to inform the contractor and end user about how our products get installed and how different configurations could benefit the application. The most important feature of this course is the opportunity for the costumers to give feed back in order for OPW to improve or address issues pertaining to our products.

## Slide 2: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
5 or 15 gallon
Cast iron or composite base
Rain tight cover or sealable cover
Drain valve or drain plug
Configurations
Notes: Fill containers can have either a drain valve or a plug but vapor containers can not have a drain valve.

## Slide 3: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Sealable Cover!
Notes: Sealable cover is offered as an option and can not be swapped out for a rain tight cover without changing the mounting ring. The mounting ring must not be changed in the field on a direct burry spill container, however a multi-port could be converted by swapping out mounting ring.

## Slide 4: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Composite Base!
Notes: Composite base spill containers have a larger throat near the base to compensate for the material strength. An FSA-400 (tall) face seal adapter can only be used on composite base containers. An JSK 4410 (tall) jack screw assembly can only be used on composite containers.

## Slide 5: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Cast Iron Base!
Notes: Cast iron base spill containers thread pattern starts immediately at the base an can therefore be used with either the FSA-400 (tall) or FSA-400S (short) face seal adapter. You must use an JSK-4410CB Jack Screw assembly.

## Slide 6: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Remove all old components off of tank riser and ensure that riser and protective coating (pipe tape) are in good operating condition.
Set the riser length “L Dimension” to the specified height.
Notes: Any metal that comes in contact with the backfill must be protected from the backfill including band clamps and tank risers. Verify the integrity of these items before installation is complete

## Slide 7: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
“L DIMENSIONS”
5 Gallon Composite Base L= 15 5/8”
5 Gallon Cast Iron Base L= 14 ½”
15 Gallon Composite Base L= 19 5/8”
15 Gallon Cast Iron Base L= 18 ½”
Notes: These L Dimensions already include the 1” slope of grade.

## Slide 8: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Clean and deburr tank riser pipe then apply a non hardening gas resistant pipe sealant the riser threads.

## Slide 9: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Before installing FSA adapter or spill container check riser torque by using TC-400 torque cap in conjunction with the 61-SA Tool
Notes: When applying proper torque apply the highest value on the tank riser and successively work down as the components get installed.

## Slide 10: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Install the FSA adapter on the tank riser using the 61-SA Tool. The proper torque value is 125-250 FT LBS Apply pipe sealant to the threads on the FSA adapter.

## Slide 11: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
FSA-400
FSA-400S
Notes: FSA-400 can be installed on both cast iron base and composite base spill containers and will add 3 ¼” to the overall “L dimension” . FSA-400 S can only be used with cast iron spill containers and will add 1 ¾” to the overall “L dimension”. Fill and tank probes are required to have an FSA adapter installed

## Slide 12: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Finish torqueing the spill container at the base with the 61-SA Tool. The proper torque is 125-250 FT LBS
Install the spill container. Make sure to stop when the container is hand tight.
Notes: Do not attempt to torque the spill container by hand this could cause separation of the bellows seals and could potentially cause the container to leak. Containers must be torqued at the base of the container with the 61-SA Tool.

## Slide 13: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Apply pipe sealant to the factory supplied pipe nipple and use the TC-400 in conjunction with the 61-SA Tool to torque the nipple down. The proper torque value is 125-250 FT LBS. Install the OPW adapter and dust cap.
Notes: Always use OPW factory supplied nipples to ensure a tight seal. The OPW factory nipple is cut on a machine lathe and is machined to have a flat sealing surface. When installing pipe nipples 61sa tool torque cap chain wrench and strap wrench can be used.

## Slide 14: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Overview
FSA-400 (Tall) can be used on both style spill containers
When installing nipples in spill containers acceptable tools include the following; 61-SA Tool, Torque Cap, Chain wrench and Strap wrench
Vapor spill containers can not have a drain valve
Fill and tank probe risers are required to have an FSA adapter installed

## Slide 15: 1-2100 SERIES DIRECT BURRY SPILL CONTAINERS
Overview
Page 101 and 102 in the manual have most of the torque and “L dimensions” listed
FSA-400S (Short) can only be used with cast iron base containers

## Slide 16: Questions?

## Slide 17: 700L/700L Remote Series Secondary Contained Spill Bucket
This product has been obsoleted, however it is still C.A.R.B approved and OPW offers still offers replacement parts.
Questions

## Slide 18: 6511-RB16 Riser Spacer
Riser spacer is designed to keep risers at 16” centers.
Notes: keeping the risers at 16” centers will help relive unwanted stress on the spill container and Multi Port assembly
It is offered in a slip fit style ( usually installed prior to FSA and spill containers) or a clamp style which could be installed as a retrofit.

## Slide 19: POMECO MULTI-PORT SPILL CONTAINMENT MANHOLE INSTALLATION
Mark off finish grade
Set multi-port assembly to the final grade.

## Slide 20: POMECO MULTI-PORT SPILL CONTAINMENT MANHOLE INSTALLATION
Remove the cover
Cut the tank risers to required height (spill container “L dimension”)

## Slide 21: POMECO MULTI-PORT SPILL CONTAINMENT MANHOLE INSTALLATION
Deburr and clean riser pipes. Verify the torque value.
Apply pipe sealant to the riser threads.

## Slide 22: POMECO MULTI-PORT SPILL CONTAINMENT MANHOLE INSTALLATION
Install the FSA adapter and torque to the specified value. The specified torque value is 125-250 FT LBS.

## Slide 23: POMECO MULTI-PORT SPILL CONTAINMENT MANHOLE INSTALLATION
Finish torqueing with the 61-SA Tool. Proper torque is 125-250 FT LBS.
Thread Spill Container on tank riser
Notes: Do not attempt to torque container by hand this could cause the seals to fail.

## Slide 24: POMECO MULTI-PORT SPILL CONTAINMENT MANHOLE INSTALLATION
Install the multi-port cover. Take precautions not to move or damage the gaskets and O-rings.
Install mounting rings and use a crows foot wrench and a torque wrench to apply the proper torque. The proper torque is 15-20 FT LBS.

## Slide 25: POMECO MULTI-PORT SPILL CONTAINMENT MANHOLE INSTALLATION
Preform regulatory compliance tests before pouring concrete.
Apply proper torque to Roto lock bolts . The proper torque is 40-50 FT LBS.

## Slide 26: POMECO MULTI-PORT SPILL CONTAINMENT MANHOLE INSTALLATION
Do Not Over Tighten !!
Follow factory torque settings
Torque in succession

## Slide 27: Retrofit & Upgrades
Special Order Multi-Ports
Measurements
Configuration
Pictures
Take your own measurements
Fill out the forms yourself
Include pictures

## Slide 28: 6521XAR Adaptor Ring
The 6521XAR Adaptor Ring is designed to replace an existing manhole with a POMECO Roto Lock style manhole
The adapter ring provides an adequate surface and stable structure for the Roto Lock to engage!

## Slide 29: Multi-Port Water Shroud
Install SLPK gasket on tank sump top hat
Apply a even bead of SL-1100 sealant to SLPK gasket groove

## Slide 30: Multi-Port Water Shroud
Install FRP fiberglass cover over spill containers and onto gasket
Install 2 shroud boots and 4 band clamps

## Slide 31: POMECO 500 Series Maintenance
Replace worn or damaged O-rings and gaskets before installing cover
Check Roto Lock Clearance
Apply grease to Roto Lock bolt, replace washers and re install Roto Locks
Thoroughly clean all gasket and O-ring sealing surfaces
Inspect Roto Locks and replace any components that have visual signs of damage
Remove all lids and cover

## Slide 32: 1DK-2100 Series Drain Valve
Clean spill container prior to removing drain valve
If replacing the valve discard all old hardware and valve
Apply grease to the new O-ring and container cavity
Install valve and new hardware and torque nuts @ 11.5 to 13.5 FT LBS

## Slide 33: 61SO-Overfill Prevention Valve
This product has been obsoleted,
However the 61SO is still C.A.R.B approved and could still be installed.

## Slide 34: 71SO-EVR Overfill Protection Valve
Following the instructions for the OPW 71SO installation will provide initial shutoff at 95%

## Slide 35: 71SO-EVR Overfill Protection Valve
Use the measuring stick provided to obtain length from inside top of the tank to the top of the FSA adapter (A)

## Slide 36: 71SO-EVR Overfill Protection Valve
Use a tape measurer to obtain the length from the bottom of the tank to the top of the FSA adapter (B)

## Slide 37: 71SO-EVR Overfill Protection Valve
If the 95% calculation requires the valve to be set at 6.5” or less use the measuring stick provided to mark the upper tube

## Slide 38: 71SO-EVR Overfill Protection Valve
If the 95% calculation requires the valve to be set at 6.5” or more measure the distance from the inside top of the tank to the top of the FSA adapter and add 6.5”

## Slide 39: 71SO-EVR Overfill Protection Valve
Mark Tube
Use band clamp to keep cut straight
Use a fine tooth hack saw and make the straightest cut possible
Notes: Fine tooth hack saw will make a clean cut. Do not use a sawzall or tube cutter it could deform the tube making it harder to insert the inltet adapter or cause it to leak after installation.

## Slide 40: 71SO-EVR Overfill Protection Valve
Use a half round file and create a good chamfer on the upper tube
Use a fine grit sand paper or emery cloth to further prepare the surface

## Slide 41: 71SO-EVR Overfill Protection Valve
Thoroughly clean the upper tube with a clean rag and acetone
Apply grease to inside of upper tube and inlet adaptor
Notes: Be sure that all of the metal shaving have vacated the valve assembly before completing the installation .

## Slide 42: 71SO-EVR Overfill Protection Valve
Insert the inlet tube
If inlet tube is not sliding into place lay a piece of 2X4 across the top and apply steady blows with a small sledge hammer until inlet is seated
Notes: Be sure the valve is not sitting on the bear concrete

## Slide 43: 71SO-EVR Overfill Protection Valve
Slide OPW 71SO-ToolC over inlet and synch down the set screw to ensure the unit does not move

## Slide 44: 71SO-EVR Overfill Protection Valve
Check the pre set drill bit before drilling first hole
Drill all 3 holes then remove the 71SO-ToolC

## Slide 45: 71SO-EVR Overfill Protection Valve
Dimple the first hole
Apply grease to the tap tight screw and install
Dimple the other two holes and install tap tight screws
Torque tap tight screws @ 20- 30 IN LBS

## Slide 46: 71SO-EVR Overfill Protection Valve
Apply grease to lower O-ring and threads
Thread lower tube onto upper tube assembly using a chain or strap wrench.

## Slide 47: 71SO-EVR Overfill Protection Valve
Measure from the top of the FSA adapter to the bottom of the tank
Subtract no more than 6 inches and mark the bottom of the tube
Cut lower tube per local code

## Slide 48: 71SO-EVR Overfill Protection Valve
Insert drop tube assembly into tank riser
Ensure the elastic band holding down the float is removed
Align the float long ways with the tank

## Slide 49: 71SO-EVR Overfill Protection Valve
Ball floats must be set higher than the 71SO valve
Continue the installation of the jack screws assembly , nipple and adapter

## Slide 50: 71SO-EVR Overfill Protection Valve
Overview
Tap tight screws get torqued @20-35 IN LBS
First step in removing the 71SO is to loosen the Jack screws assembly
No epoxy is required to install the 71SO
To obtain top tube measurement the dimension is recorded from the inside of tank bung to the top of the FSA

## Slide 51: 71SO-EVR Overfill Protection Valve
Overview
When using the 71SO ball valves must be installed higher than the overfill valve
Things that could cause the upper inlet tube to fail; over tightening the jack screws, not cutting the upper tube square, and tightening the nipple in the spill container after tightening the jackscrews

## Slide 52: 6111-1400 Tank Bottom Protector
If a tank bottom protector is installed always reinstall the unit when changing drop tubes
Drill 3 holes in the specified areas and install the supplied pop rivets

## Slide 53: 61JSK Jack Screw Assembly's
61JSK-44CB 61JSK-4410

## Slide 54: 61JSK Jack Screw Assembly's
Insert lower cage into spill container and place on top of the drop tube with the screw beds facing up
Apply Lock Tight to screw threads and loosely thread screws into the upper cage

## Slide 55: 61JSK Jack Screw Assembly's
Insert the upper cage into spill container on top of the lower cage making sure the screws sit in the beds
Install Nipple
Use ¼” Allen socket and evenly torque screws @ 3.5 to 5 IN LBS

## Slide 56: 61SALP EVR Rotatable Product Adapter
Thread on spill container nipple use 61SA Tool and torque @ 90 to 110 FT LBS
Static torque of 108 IN LBS or less
Replacement parts:
Nipple sealing gasket OPW P/N H09039M

## Slide 57: 61VSA EVR Rotatable Vapor Recovery Adapter
Thread on spill container nipple use 61SA Tool and torque @ 90 to 110 FT LBS
Static torque of 108 IN LBS or less
Replacement Parts:
Nipple sealing gasket OPW P/N H09039M
Vapor poppet Kit
OPW P/N 61VSA-KIT

## Slide 58: 623 Pressure Vacuum Vent
This product has been De-certified , however if it is still installed it will require a annual visual inspection and cleaning. The unit can remain in service until May 30th 2012
Questions?

## Slide 59: Installation Tools
61SA-Tool
TC-400 TORQUE CAP

## Slide 60: Registration Card
Fill registration cards out and send them in to OPW

## Slide 61: Torque Specifications

## Slide 62: “L” Dimensions

## Slide 63: 1-3100 Series Spill Containers
Edge single wall will require the use of an FSA adaptor
Edge single wall “L” dimension 5 gallon cast iron base with FSA-400S: 151/2”

## Slide 64: 1-3100 Series Spill Containers
Edge double wall spill container “L” dimension: 15 5/8”

## Slide 65: 1-3100 Series Primary and Secondary Bucket Replacement Instructions
The Edge single wall and double wall Bucket comes fully assembled and will not require disassembly to install!

## Slide 67: 1-3100 Series Spill Containers
Questions